# MANGALORE REFINERY AND PETROCHEMICALS LIMITED

HOT WORK & NAKED FLAME PERMIT — FORM B (OISD-STD-105)

───────────────────────────────────────────────────────

| Permit Serial No: | HW-MRPL-20260828-042 |
| --- | --- |
| Plant / Location: | Crude Distillation Unit (CDU-1) - Column Overhead |
| Validity Window: | 2026-08-28 08:00 to 18:00 hrs |
| Designated Firewatch: | Mr. Ramesh Kumar (ID: FW-8841) |

# 1. Multi-Gas Atmospheric Test Matrix (Pre-Entry & Periodic)

| Atmospheric Gas Parameter | Permissible Safe Limit | Measured Test Value | Status |
| --- | --- | --- | --- |
| Combustible Hydrocarbons (%LEL) | 0.0% (Strictly Nil) | 0.0% | PASS - SAFE |
| Oxygen Content (O₂ %) | 19.5% - 23.5% | 20.8% | PASS - SAFE |
| Hydrogen Sulphide (H₂S ppm) | < 10.0 ppm (Ceiling) | 0.0 ppm | PASS - SAFE |
| Carbon Monoxide (CO ppm) | < 35.0 ppm | 2.1 ppm | PASS - SAFE |

# 2. Mandatory Safety & Isolation Checkpoints

[X] Equipment positively blinded / spaded with blind register entry.

[X] Sewers, catch basins, and oily water drains within 15m covered with fire blankets.

[X] Continuous pressurized fire hose and two 10kg DCP extinguishers stationed at site.

[X] LOTO Certificate issued for electrical drive isolation.

# 3. Issuing & Receiving Authority Sign-off Ladder

| Gas Analyst / QA-QC: ___________________ Instrument QC Specialist | Issuing Authority: ___________________ Shift In-Charge (Operations) | Accepting Authority: ___________________ Executing Engineer (Maintenance) |
| --- | --- | --- |